SECTION 01810

COMMISSIONING REQUIREMENTS

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

Notes:  This Section is intended to include commissioning procedures and submittals.

Include the appropriate portions of Sections 02996, 02997, 02998, 13896, 13897, 13898, 13996, 13997, 13998, 14996, 14997, 14998, 15996, 15997, 15998, 15999, 16996, 16997, and 16998 in the Technical Specifications.

Delete this Section if no equipment/systems are to be commissioned.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

PART 1	GENERAL

1.01	DESCRIPTION

A.	Commissioning.  Commissioning is a systematic process of to ensure that all building systems and equipment perform interactively according to the design intent and the Owner’s operational needs.    The commissioning process shall encompass and coordinate the traditionally separate functions of system documentation, equipment startup, control system calibration, testing and balancing, performance testing, and training.

Commissioning shall:

1)	Verify that applicable equipment and systems are installed according to the manufacturer’s recommendations and industry accepted minimum standards and that they receive adequate operational checkout by installing contractors.

2)	Verify and document proper performance of equipment and systems.

3)	Verify that O&M documentation left on site is complete.

4)	Verify that the Owner’s operating personnel are adequately trained.

- The commissioning process does not take away from or reduce the responsibility of the system designers or installing contractors to provide a finished and fully functioning product.

- DEFINITIONS

Acceptance Phase - Phase of construction after startup and initial checkout when functional performance tests, O&M documentation review, and training occur.

Approval - Acceptance that a piece of equipment or system has been properly installed and is functioning in the tested modes according to the Contract Documents.

Commissioning Agent (CA) – The Owner assigned individual who   coordinates the day-to-day commissioning activities, on behalf of the Owner and the PM.  The CA shall not take an oversight role on day-to-day construction activities.

Commissioning Plan - An overall plan, developed by the Contractor that provides the structure, schedule and coordination planning for the commissioning process.

Control system – A component of environmental, security, and fire systems for reporting/monitoring and issuing of commands to/from field devices.

Data logging  The monitoring and recording of flows, currents, status, pressures, etc., of equipment using stand-alone data recorders separate from the control system or the trending capabilities of control systems.

Deferred Functional Tests (DFTs)  Functional Tests that are performed, at the discretion of the CA, after Substantial Completion, due to partial occupancy, equipment, seasonal requirements, design, or other site conditions that disallow the test from being performed.

Deficiency - A condition in the installation or function of a component, piece of equipment, or system that is not in compliance with the Contract Documents.

Factory Testing - Testing of equipment on-site or at the factory, by factory personnel, with or without an Owner’s representative present.

Functional Test (FT) – Performance testing of the dynamic functions and operations of equipment and systems using manual (direct observation) or monitoring methods. Functional testing is the dynamic testing of systems (rather than just components) under full operation (e.g., the chiller pump is tested interactively with the chiller functions to see if the pump ramps up and down to maintain the differential pressure setpoint).  Systems are tested under various modes, such as during low cooling loads, high loads, component failures, unoccupied, varying outside air temperatures, fire alarm, power failure, etc.  The systems are run through all the control system’s sequences of operation and components are verified to be responding as the sequences state. FTs are performed after prefunctional checklists and startup are complete.

Manual Test - Using hand-held instruments, immediate control system readouts, or direct observation to verify performance (contrasted to analyzing monitored data taken over time to make the “observation”).

Non-Compliance - See Deficiency.

Non-Conformance - See Deficiency.

Over-ridden Value - Riding over a sensor value in the equipment’s controls to observe the response of of the equipment’s operation (e.g., changing the outside air temperature value from 50F to 75F to verify economizer operation).  See also “Simulated Signal.”

Owner-Contracted Tests - Tests paid for by the Owner.  These tests will not be repeated during functional testing if successful and properly documented.

Phased Commissioning - Commissioning that is completed in phases (by floors, for example) due to the size of the structure or other scheduling issues.

Prefunctional Checklist  - A list of items to inspect and elementary component tests to conduct to verify proper installation of equipment.  Prefunctional checklists are primarily static inspections and procedures to prepare the equipment or system for initial operation (e.g., belt tension, oil levels, labels affixed, gages in place, sensors calibrated, etc.).  However, some prefunctional checklist items entail simple testing of the function of a component, a piece of equipment or system (such as measuring the voltage imbalance on a three phase motor).  The word prefunctional refers to before functional testing.  Prefunctional checklists augment and are combined with the manufacturer’s start-up checklist. All Prefunctional Checklist  items must be satisfactory prior to the FT.

Sampling - Functionally testing only a fraction of the total number of identical or near identical pieces of equipment.  Refer to Paragraph 3.04 F for details.

Seasonal Functional Tests – Performance FTs that are deferred until the system(s) will experience conditions closer to their design conditions.

Simulated Condition - Condition that is created for the purpose of testing the response of a system (e.g., raising/lowering the setpoint of a thermostat to see the response in a VAV box).

Simulated Signal - Disconnecting a sensor and using a signal generator to simulate a sensor value for the purpose of testing a full range of conditions.

Startup - The initial starting or activating of dynamic equipment, including executing prefunctional checklists.

Test Requirements - Requirements specifying what modes and functions, etc., shall be tested and the acceptable range of performance limits that must be met.  The test requirements are specified in the Technical Specifications Sections of the Contract Documents.

Trending – Monitoring, using the building management system, whereby data gathered over a period of time is compiled for analysis.

Vendor - Supplier of equipment.

Warranty Period – Refer to Section 01740.

1.02	COORDINATION

A.	Project Commissioning Team.  The members of the Project Commissioning Team will consist of the MDAD Commissioning Team (the assigned Commissioning Agent and any support personnel), the MDAD  Project Manager (PM) or designee, the Field Representative, the General Contractor Subcontractors and/or Vendors as required , and the Architect/  Engineer (A/E).

B.	Management. The CA coordinates the commissioning activities through the FR.  All members shall work together to fulfill their contracted responsibilities and meet the objectives of the Contract Documents. Refer to Paragraph 1.06 for additional management details.

C.	Scheduling.  The CA, through the FR, will provide sufficient notice to the Contractor for scheduling commissioning activities with respect to the Owner participation.  The Contractor will integrate all commissioning activities into the Overall Project Schedule. All parties will address scheduling problems and make necessary notifications in a timely manner in order to expedite the commissioning process.

  - COMMISSIONING PLAN

A. The Contractor shall develop the Commissioning Plan which shall be included in the Project Schedule when approved by the Owner. The following narrative provides a brief overview of the typical commissioning tasks during construction and the general order in which they occur.

1.	Commissioning during construction begins with an initial commissioning meeting conducted by the CA where the commissioning process is reviewed with the project commissioning team members.

2.	Additional meetings will be required throughout construction, scheduled by the CA, through the FR, with necessary parties attending, to plan, scope, coordinate, schedule future activities and resolve problems.

3.	Equipment documentation is submitted to the CA, through the FR, during normal submittals, including detailed start-up procedures.

4.	The Prefunctional Checklists are to be completed by the Contractor (or its subcontractors), during the startup process.

5.	In general, the checkout and performance verification proceeds from simple to complex; from component level to equipment to systems and intersystem levels with Prefunctional Checklists being completed before functional testing.

6.	Items of non-compliance in material, installation, or setup are corrected at no expense to the Owner.

7.	The Contractor ensures that the Subcontractors’ Prefunctional Checklists are executed and documented  and that startup and initial checkout are performed.  The CA documents that the checklists and startup were completed according to the approved plans. This may include the CA witnessing start-up of selected equipment. Any testing failure is to be corrected at no additional cost to the Owner, and a re-test performed, observed, and documented.

8.	The A/E, Field Representative, and Subcontractors review and finalize the specific equipment and system functional performance test procedures.  The forms are approved by the CA.

9.	The procedures are executed by the Subcontractors, under the direction of the Field Representative, and documented by the CA.

10.	The CA reviews the O&M documentation for completeness.

11.	Commissioning is completed before Substantial Completion.

12.	The CA reviews, pre-approves, and coordinates the training provided by the Subcontractors/Contractor and verifies that it was completed.

13.	Deferred testing is conducted, as specified or required.

1.04	RELATED REQUIREMENTS

A. Section 01040			Coordination

B. Section 01300			Submittals

C. Section 01311, 01312, or 01313	Project Schedules

D. Section 01701			Contract Closeout Procedures

E. Section 01720			Project Record Documents

F. Section 01740			Warranties and Guarantees

G. Section 02996			Sitework Commissioning

H. Section 02997			Sitework Prefunctional Checklists

I. Section 02998			Sitework Functional Testing Requirements

J. Section 13896			Building Management and Control Systems Commissioning

K. Section 13897			Building Management and Control Systems Prefunctional Checklists

L. Section 13898			Building Management and Control Systems Functional Testing Requirements

M. Section 13996			Special Construction Commissioning

N. Section 13997			Special Construction Prefunctional Checklists

O. Section 13998			Special Construction Functional Testing Requirements

P. Section 14996			Conveying Equipment Commissioning

Q. Section 14997			Conveying Equipment Prefunctional Checklists

R. Section 14998			Conveying Equipment Functional Testing Requirements

S. Section 15996			Mechanical Systems Commissioning

T. Section 15997			Mechanical Systems Prefunctional Checklists.

U. Section 15998			Mechanical Systems Functional Testing Requirements

V. Section 15999			HVAC Commissioning, Testing Adjusting and Balancing

W. Section 16996			Electrical Systems Commissioning

X. Section 16997		Electrical Systems Prefunctional Checklists.

Y. Section 16998		Electrical Systems Functional Testing Requirements

1.05	RESPONSIBILITIES

A.	The general responsibilities of various parties in the commissioning process are provided in this sub-section.  The specific responsibilities are in the Technical Specifications.

B.	All Parties

1.	Follow the commissioning plan.

- Attend initial commissioning meeting, and additional meetings as necessary.

C.	Contractor

1.	Construction and Acceptance Phase

- Facilitate the coordination of the commissioning and incorporate commissioning activities (the Commissioning Plan) into the Overall Project Schedule (OPS).

- Include the cost of commissioning in the total contract price.

- Ensure that all Subcontractors and Vendors execute their commissioning responsibilities according to the Contract Documents and the OPS.

- Provide copies of all submittals as required in Section 01300 including all changes thereto.

- A representative shall attend an initial commissioning meeting and all other necessary meetings to facilitate the commissioning process and provide the initial and updated commissioning schedules.

- No later than 60 days prior to startup of the first piece of major equipment, meet with the CA, Field Representative, A/E, and PM/Owner to finalize the detailed commissioning procedures/ schedule.

- Coordinate the training of Owner personnel.

- Prepare O&M manuals, according to the Contract Documents, including clarifying and updating the original sequences of operation to as-built/as-tested conditions.

2.	Warranty Period

a.	Ensure that Subcontractors execute seasonal or deferred functional performance testing, witnessed by the CA, according to the specifications.

- Ensure that Subcontractors correct deficiencies and make necessary adjustments to O&M manuals and as-built drawings for applicable issues identified in any seasonal testing.

- Perform all guarantee  work for materials furnished under the contract for the time specified in the Contract, including all warranties and curing all latent defects within the time period provided in Section 95.11(3)(c), Florida Statutes

D.	Vendors/Subcontractors

a.	Provide all requested submittal data, including detailed start-up procedures and specific responsibilities of the Owner to keep warranties in force.

b.	Assist in equipment testing per agreements with Subcontractors and/or Contractor.

c.	Include cost of all special tools and instruments (only available from vendor, specific to a piece of equipment) required for testing, operating, and maintaining equipment according to these Contract Documents in the base bid price to the Contractor.

d.	Analyze specified products and verify that the A/E has specified the newest, most current equipment reasonable for this project’s scope and budget.

e.	Provide requested information regarding equipment sequence of operation and testing procedures.

f.	Review test procedures for equipment installed by factory representatives.

1.06	EQUIPMENT/SYSTEMS TO BE COMMISSIONED

A.	The following equipment/systems will be commissioned in this project, as indicated by “X.”

- ____	Chiller(s) and chiller loop (with chiller pumps)

- ____	Cooling tower(s) and condenser water system (with pumps and water treatment system)

- ____	Primary chilled water system (with Bridge-Tender system and primary chilled water pumps)

- ____	Secondary chilled water system (with Bridge-Tender system and secondary chilled water pumps)

- ____	Air Handling Units (with supply, return and outside air duct, variable air volume boxes, air distribution, and temperature control system)

- ____	Exhaust air systems (including fans, ductwork and interconnection with air handling/supply systems)

- ____	Supply or make-up air systems (including fans, ductwork and interconnection with air handling and/or exhaust systems)

- ____	Specialty air removal/ventilation systems (including fans, ductwork and interconnection with air handling/supply systems)

- ____	Smoke control systems (including fans, ductwork and interconnection with air handling/supply systems -in conjunction with Fire Department)

- ____	Equipment vibration monitoring systems (including sensors, transmitters and software)

- ____	Refrigerant monitoring systems (including sensors, transmitters and exhaust/ventilation systems)

- ____	Thermal storage systems (including ice tanks, glycol chillers, pumps, heat exchangers, piping and controls)

- ____	Preconditioned air system (including chillers, ice equipment, air handling units, piping and controls)

- ____	Compressed air system for building/equipment/systems control (including compressors, receivers, piping, and air dryers)

- ____	Potable water system (including backflow preventers, fixtures, piping and water heaters)

- ____	Sanitary drainage/sewer system

- ____	Storm drainage system

- ____	Fire protection system (in conjunction with Fire Department)

- ____	Fire alarm/detection system (in conjunction with Fire Department)

- ____	Jet fuel system (in conjunction with MDAD Environmental)

- ____	Emergency power system (including emergency generator, automatic transfer switch and fuel oil system)

- ____	400 hertz system

- ____	Lighting systems (interior, exterior and/or airfield)

- ____	Switchgear, transformers, panelboards and/or motor control centers

- ____	Lightning protection and/or surge suppression system

- ____	Public address, closed circuit TV, flight information display and/or telephone systems

- ____	Doors security system

- ____	Kitchen, cooking, and/or food preparation systems

- ____	Escalator and/or elevator systems

- ____	Automatic people mover system and/or moving walkways

- ____	Baggage conveyor, make-up and claim systems

- ____	Passenger loading bridges

- ____	Doors and hardware

- ____	Irrigation system

- ____	Walk-in coolers and/or freezers

- ____	HVAC, Test, Adjust, and Balance

- ____	[Other]

PART 2	PRODUCTS

2.01	TEST EQUIPMENT

A.	All standard testing equipment required to perform startup and initial checkout and required functional performance testing shall be provided by the Contractor for the equipment being tested.  This includes, but is not limited to, two-way radios, meters, and data recorders.

B.	Special equipment, tools, and instruments required for testing equipment according to these Contract Documents shall be included in the Contractor’s base bid price and shall be turned over to the Owner at Project close-out.

C.	All testing equipment shall be of sufficient quality and accuracy to test and/or measure system performance within the tolerances specified in the Specifications. If not otherwise noted, the following minimum requirements apply:  Temperature sensors and digital thermometers shall have a certified calibration within the past year to an accuracy of 0.5 degree F and a resolution of  + or - 0.1 degree F.  Pressure sensors shall have an accuracy of + or - 2.0% of the value range being measured (not full range of meter) and have been calibrated within the last year.  All equipment shall be calibrated according to the manufacturer’s recommended intervals and when dropped or damaged.  Calibration tags shall be affixed or certificates readily available.

PART 3 - EXECUTION

3.01	MEETINGS

A.	Initial Meeting.  Within 10 days of the Notice to Proceed (NTP), the CA, through the FR, will schedule, plan and conduct an initial commissioning meeting.  The Contractor and its responsible parties are required to attend.

B.	Miscellaneous Meetings.  Other meetings will be planned and conducted by the CA as construction progresses.  These meetings will cover coordination, deficiency resolution, and planning issues.  These meetings will be held at least monthly, until the final 3 months of construction, when they may be held as frequently as one per week.

3.02	START-UP, PREFUNCTIONAL CHECKLISTS, AND INITIAL CHECKOUT

A.	The following procedures apply to all equipment/systems to be commissioned, according to Paragraph 1.06 Equipment/Systems to be commissioned.

B.	General.  Prefunctional checklists are important to verify that the equipment and systems are fully connected and operational.  It ensures that functional performance testing (in-depth system checkout) may proceed without unnecessary delays.  Each piece of equipment shall receive full prefunctional checkout.  No sampling strategies shall be used.  The prefunctional testing for a given system must be successfully completed prior to formal functional performance testing of equipment or subsystems of the given system.

- Start-up and Prefunctional Checkout Plan.  The CA shall assist the project commissioning team members responsible for startup of any equipment.  The primary role of the CA in this process is to ensure that there is written documentation that each of the manufacturer-recommended procedures has been completed.  Parties responsible for prefunctional checklists and startup shall be identified in the commissioning scoping meeting and on the checklist forms.  Parties responsible for executing functional performance tests are identified in the testing requirements in the Technical Specifications.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

The A/E shall update or provide additional prefunctional checklists as necessary

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

- The prefunctional checklists are provided in the Technical Specifications. These checklists indicate required procedures to be executed as part of startup and initial checkout of the systems and the party responsible for their execution.

- The Contractor shall determine which trade is responsible for executing and documenting each of the line item tasks and transmit the checklists to the responsible Subcontractors.  Each form may have more than one trade responsible for its execution.

- The subcontractor responsible for the purchase of the equipment shall develop the full start-up plan by combining the manufacturer’s detailed start-up and checkout procedures and the prefunctional checklists.

- The subcontractor shall submit the full startup plan to the Contractor for review and approval by the CA.

- The CA will review and approve the procedures and the documentation format for  (noting any procedures that need to be added). The CA will return the procedures and the documentation format to the Contractor, through the FR.

6.	The Contractor will transmit the full start-up plan to the Subcontractors for their review and use.

D.	Sensor and Actuator Calibration. All field-installed temperature, relative humidity, CO, CO2, refrigerant, O2, and/or pressure sensors and gages, and all actuators (dampers and valves) on all equipment shall be calibrated.  Verify that all locations are appropriate and away from causes of erratic operation.  Submit to the FR calibration methods and results.  All test instruments shall have had a certified calibration within the last 12 months, and comply with all local, state and/or federal requirements/certifications, as required.  Sensors installed in the unit at the factory with calibration certification provided need not be field calibrated.

All procedures used shall be fully documented on the prefunctional checklists, as an attachment, or other suitable forms, clearly referencing the procedures followed, and stating the initial, intermediate, and final results.

E.	Execution of Prefunctional Checklists and Startup.

1.	Four weeks prior to the scheduled startup, the Subcontractors and Vendors shall coordinate startup and checkout with the Field Representative, A/E, Contractor, PM,and CA.  The execution of the prefunctional checklists, startup, and checkout shall be directed and performed by the Subcontractor or Vendor.  Signatures are required of the applicable Subcontractors for verification of completion of their work.

2.	The PM, CA, Field Representative, and A/E as necessary, shall observe, at minimum, the procedures for each piece of primary equipment, unless there are multiple units, in which case a sampling strategy may be used.  In no case will the number of units witnessed be less than four on any one building, nor less than 20% of the total number of identical units.

3.	For lower-level components of equipment, (e.g., sensors, controllers), the CA shall observe a sampling of the prefunctional and start-up procedures.

4.	The Subcontractors and Vendors shall execute startup and provide the CA and A/E, through the FR, with a signed and dated copy of the completed start-up and prefunctional tests and checklists.

5.	Only individuals of the Contractor (technicians, engineers, tradesmen, vendors, etc.) who have direct knowledge and witnessed that a line item task on the prefunctional checklist was actually performed shall check off that item.  It is not acceptable for witnessing supervisors to fill out these forms.

F.	Deficiencies, Non-Conformance, and Approval in Checklists and Startup.

1.	The Contractor shall ensure that the Subcontractors clearly list any outstanding items of the initial start-up and prefunctional procedures that were not completed successfully, on an attached sheet.  The form and any outstanding deficiencies shall be provided, through the FR, to the CA within two days of test completion.

2.	The CA will review the report and issue either a non-compliance report or an approval form, through the FR, to the Contractor.  The installing Subcontractors or vendors shall correct all areas that are deficient or incomplete in the checklists and tests in a timely manner, shall notify the FR as soon as outstanding items have been corrected, and resubmit an updated start-up report with a Statement of Correction on the original non-compliance report.  When satisfactorily completed, the CA will recommend approval of the execution of the checklists and startup of each system.

- Items left incomplete, which later cause deficiencies or delays during functional testing may result in backcharges to the Contractor.  Refer to Paragraph 3.05, herein, for details.

3.03	PHASED COMMISSIONING

A.	The project may require startup and initial checkout to be executed in phases.  Phasing shall be coordinated with the PM, CA, A/E, and Contractor and reflected in the Overall Project Schedule and commissioning schedule by the Contractor.

3.04	FUNCTIONAL TESTING

A.  The functional testing shall demonstrate that each system is operating according to the documented design intent and Contract Documents.  Functional testing facilitates bringing the systems from a state of individual substantial completion to full dynamic operation. Additionally, during the testing process, areas of deficient performance are identified and corrected, improving the operation and functioning of the systems.

B.Coordination and Scheduling.  The Contractor shall provide sufficient notice, regarding their completion schedule for the prefunctional checklists and startup of all equipment and systems to allow the functional performance testing to be scheduled The Commissioning Team shall oversee, witness, and document the functional testing of all equipment and systems. The Contractor/Subcontractors shall execute the tests. Functional testing shall be conducted after prefunctional testing and startup has been satisfactorily completed.  The control system shall be sufficiently tested and approved by the CA before it is used,  to verify performance of other components or systems.  The air balancing and water balancing shall be completed before functional testing of air-related or water-related equipment or systems.  Testing proceeds from components to sub- systems to systems.  When the proper performance of all interacting individual systems has been achieved, the interface or coordinated responses between systems shall be checked.

C.	Development of Test Procedures.  Before test procedures are finalized, the Contractor shall provide to the A/E and the CA all requested documentation and a current list of changes affecting equipment or systems, including an updated points list, program code, control sequences, and testing parameters.  Using the testing parameters and requirements in the Technical Specifications, the A/E shall update/develop specific test procedures and forms to verify and document proper operation of each piece of equipment and system.  Each Subcontractor or Vendor, as appropriate, shall provide assistance to the A/E in developing the final procedures (answering questions about equipment, operation, sequences, etc.).  Prior to finalization, the A/E shall provide a copy of the test procedures to the Contractor who shall review the tests for feasibility, safety, equipment, and warranty protection.  The final test forms shall be submitted to the CAfor review and approval.

D.	Test Methods.

1.	Functional testing and verification may be achieved by manual testing or by monitoring the performance and analyzing the results using the control system’s trend log capabilities or by stand-alone data loggers.  The CA may substitute specified methods or require an additional method to be executed, other than what was specified, with the approval of the Contractor, A/E, and PM. The CA will determine which method is most appropriate for tests that do not have a method specified.

2.	Simulated Conditions.  Simulating conditions (not by an overridden value) shall be allowed, though timing the testing to experience actual conditions is encouraged wherever practical.

3.	Overridden Values.  Overriding sensor values to simulate a condition, such as overriding the outside air temperature reading in a control system to be something other than it really is, is allowed, but shall be used with caution and avoided when possible.  Sensors, transducers and devices shall have been calibrated  before simulating conditions or overriding values,.

4.	Simulated Signals.  Using a signal generator which creates a simulated signal to test and calibrate transducers and DDC constants is generally recommended over using the sensor to act as the signal generator via simulated conditions or overridden values.

5.	Altering Setpoints.  Rather than overriding sensor values, and when simulating conditions is difficult, altering setpoints to test a sequence is acceptable.

6.	Indirect Indicators.  Relying on indirect indicators for responses or performance shall be allowed only after visually and directly verifying and documenting, over the range of the test parameters, that the indirect readings through the control system represent actual conditions and responses.

7.	Setup.  Each function and test shall be performed under conditions that simulate actual conditions as closely as is practically possible.  The Subcontractor(s) executing the test shall provide all necessary materials, system modifications, etc., to produce the necessary flows, pressures, temperatures, etc., necessary to execute the test according to the specified conditions.  At completion of the test, the Subcontractor(s) shall return all affected equipment and systems to their approved operating settings.

8.	Sampling.  Multiple identical pieces of non-life-safety or otherwise non-critical equipment may be functionally tested using a sampling strategy, when when requested by the Contractor and approved by the CA.  Significant application differences and significant sequence of operation differences in otherwise identical equipment invalidates their common identity.  A small size or capacity difference, alone, does not constitute a difference.  No sampling by Subcontractors shall be allowed in prefunctional checklist execution.

A common sampling strategy is the xx% Sampling yy% Failure Rule. It is defined by the following example.

xx = the percent of the group of identical equipment to be included in each sample.

yy = the percent of the sample that if failing, will require another sample to be tested.

The example below describes a 20% Sampling, 10% Failure Rule.

a.	Randomly test at least 20%  of each group of identical equipment. In no case test less than three units in each group.  This 20%, or three, constitute the “first sample.”

b.	If 10%  of the units in the first sample fail the functional performance tests, test another 20% of the group (the second sample).

c.	If 10% of the units in the second sample fail, test all remaining units in the whole group.

d.	If at any point frequent failures are occurring and testing is becoming more timeconsuming than verification, the CA may stop the testing and require the responsible Subcontractor to perform and document a checkout of the remaining units, prior to continuing with functionally testing the remaining units.

E.	Test Equipment.  Refer to Part 2 for test equipment requirements.

F.	Problem Solving.  The burden of responsibility to solve, correct, and retest malfunctions/failures is with the Contractor, with A/E approval as required.

3.05	DOCUMENTATION, NON-CONFORMANCE, AND APPROVAL OF TESTS

A.	Documentation.  The CA shall witness and verify/approve the documentation of the results of all functional performance tests.

B.	Non-Conformance.

1.	Corrections of minor deficiencies identified may be made during the tests at the discretion of the CA.  In such cases the deficiency and resolution will be documented on the procedure form or on an attached sheet.

2.	As tests progress and a deficiency is identified, the CA shall discuss the issue with the Commissioning Team, and the Contractor.

a.	When there is no dispute on the deficiency and the Contractor accepts responsibility to correct it:

1)	The CA will document the deficiency and the Contractor’s response and intentions. After the day’s work, the CA will submit the non-compliance reports to the PM.  The Contractor corrects the deficiency, signs the statement of correction at the bottom of the non-compliance form certifying that the equipment is ready to be retested and sends it back to the CA.

2)	The Contractor shall reschedule the test; and the test  repeated.

b.	If there is a dispute about a deficiency, regarding whether or not it is a deficiency:

1)	The dispute shall be documented on the non-compliance form with the Contractor’s  response.

2)	Resolutions are made at the lowest management level possible.  Other parties are brought into the discussions as needed.  Final interpretive authority is with the A/E.  Final acceptance authority is with the Project Manager.

3)	The CA documents the resolution process.

4)	Once the interpretation and resolution have been decided, the Contractor corrects the deficiency, signs the statement of correction on the non-compliance form and provides it to the PM, through the Field Representative,.  The Contractor shall reschedule the test and the test repeated until satisfactory performance is achieved.

3.	Cost of retesting a prefunctional or functional testshall be the Contractor’s.

4.	The Contractor shall submit, in writing to the FR, at least as often as commissioning meetings are being scheduled, the status of each outstanding discrepancy identified during commissioning. Discussion shall cover explanations of any disagreement and proposals for their resolutions.

a.	The CA retains the original non-conformance forms until the end of the project.

b.	Retesting shall not be considered a justified reason for a claim of delay or for a time extension by the Contractor.

C.	Failure Due to Manufacturer Defect.  If 10%, or three, whichever is greater, of identical pieces (size alone does not constitute a difference) of equipment fail to perform to the Contract Documents (mechanically or substantively) due to a manufacturing defect not allowing it to meet its submitted performance specification, all identical units may be considered unacceptable by the A/E or PM. In such case, the Contractor shall provide the Owner with the following:

a.	Within one week of notification from the Field Representative, the Contractor or manufacturer’s representative shall examine all other identical units making a record of the findings.  The findings shall be provided to the Field Representative within two weeks of the original notice.

b.	Within two weeks of the original notification, the Contractor or manufacturer shall provide a signed and dated, written explanation of the problem, cause of failures, etc., and all proposed solutions.  The proposed solutions shall not significantly exceed the specification requirements of the original installation.

c.	The A/E will determine whether a replacement of all identical units or a repair is acceptable.

d.	Two examples, where applicable, of the proposed solution shall be installed by the Contractor and the A/E shall be allowed to test the installations for up to one week, upon which the A/E will decide whether to accept the solution.

e.	Upon acceptance, the Contractor and/or manufacturer shall replace or repair all identical items, at their expense.  The replacement/repair work shall proceed with reasonable speed beginning within one week from when parts can be obtained.

D.	Approval.  The CA notes each satisfactorily demonstrated function on the test form. Final approval of the functional test is made after review by the CA and PM, following recommendations by the A/E and Contractor.

3.06	DEFERRED TESTING

A.	Unforeseen Deferred Tests.  If any check or test cannot be completed due to the project completion level, required occupancy condition or other deficiency, execution of checklists and functional testing may be delayed upon approval of the PM.  These tests will be conducted in the same manner as the seasonal tests as soon as possible.  Services of necessary parties will be negotiated.

- Seasonal Testing.  During the warranty period, seasonal testing (tests delayed until weather conditions are closer to the system’s design) specified in Section 15997 shall be completed as part of this contract.  The CA shall coordinate this activity, through the PM.  Tests will be executed, documented and deficiencies corrected by the appropriate Subcontractors, with the CA witnessing.  Any final adjustments to the O&M manuals and as-builts due to the testing shall be made by the Contractor.

3.07	TRAINING OF OWNER PERSONNEL

- The Contractor shall provide training coordination, scheduling of subcontractors, and ensure that training is completed. All training shall be coordinated, through the Field Representative, with the PM.

- The Contractor shall ensure that each Subcontractor and Vendor (mechanical, plumbing, fire, electrical, specialty, etc.) shall have the following responsibilities:

1.	Provide, through the Field Representative, the PM with a training plan sixty days before the planned training covering the following elements:

a.	Equipment

b.	Intended audience

c.	Location of training

d.	Objectives

e.	Subjects covered  (description, duration of discussion, special methods, etc.)

f.	Duration of training on each subject

g.	Instructor for each subject

h.	Methods (classroom lecture, manufacturer’s quality video, site walk-through, actual operational demonstrations, written handouts, etc.).

2.	Provide designated Owner personnel with comprehensive orientation and training in the understanding of the systems and the operation and maintenance of each piece of equipment that makes up the system.

3.	Training shall normally start with classroom sessions followed by hands-on demonstration/training on each piece of equipment.

4.	During any demonstration, should the system fail to perform in accordance with the requirements of the O&M manual or sequence of operations, the system shall be repaired or adjusted as necessary and the demonstration repeated at another scheduled time, if necessary.

5.	The appropriate trade or manufacturer's representative shall provide the instructions on each major piece of equipment.  Practical building operating expertise as well as in-depth knowledge of all modes of operation of the specific piece of equipment are required.  More than one party may be required to execute the training.

6.	The controls contractor shall attend sessions other than the controls training, as specified, to discuss the interaction of the controls system as it relates to the equipment being discussed.

7.	The training sessions shall follow the outline in the Table of Contents of the operation and maintenance manual and illustrate whenever possible the use of the O&M manuals for reference.

8.	Training shall include:

a.	Use of the printed installation, operation and maintenance instruction material included in the O&M manuals.

b.	A review of the written O&M instructions emphasizing safe and proper operating requirements, preventative maintenance, special tools needed and spare parts inventory suggestions.  The training shall include start-up, operation in all modes possible, shutdown, seasonal changeover and any emergency procedures.

c.	Discussion of relevant health and safety issues and concerns.

d.	Discussion of warranties and guarantees.

e.	Common troubleshooting problems and solutions.

- Explanatory information included in the O&M manuals.

- Discussion of any peculiarities of equipment installation or operation.

- Classroom sessions shall include the use of overhead projections, slides, video/audio-taped material as might be appropriate.

- Hands-on training shall include start-up, operation in all modes possible, including manual, shut-down, alarms, power failure and any emergency procedures, and preventative maintenance for all pieces of equipment.

- The contractor shall fully explain and demonstrate the operation, function and overrides of any local packaged controls, not controlled by the central control system.

- Training shall occur after functional testing is complete, unless approved otherwise by the Project Manager.

- Videotaping of the training sessions will be provided by the Contractor and added to the O&M manuals.  In addition, factory training videos identifying key troubleshooting, repair, service and/or replacement techniques shall be provided and reviewed with the Owner.

- The responsible design or systems engineer shall at the beginning of each training session present the overall system design concept and the design concept of each equipment section.

3.08	OPERATIONS AND MAINTENANCE MANUALS/DATA

- The commissioning process requires detailed O&M documentation as identified in this section and Technical Specifications.

- Contractor shall  submit two draft copies of the complete operating and maintenance manual to the Field Representative for review by the Architect/Engineer and CA within 60 calendar days after review of equipment shop drawings.  One copy will be returned to the Contractor within 30 days after receipt by the A/E.

- Contractor shall submit corrected final approved manuals prior to Substantial Completion.  Prior to final submittal, the CA shall review the O&M manuals (in addition to the initial draft O & M manual), and documentation, with redline as-builts, for systems that were commissioned to verify compliance with the Specifications.  The CA will communicate, through the Field Representative, deficiencies in the manuals to the Contractor, PM or A/E, as requested. Upon a successful review of the corrections, the CA will recommend approval and acceptance of these sections of the O&M manuals to the PM. The CA will also review each equipment warranty and verify that all requirements to keep the warranty valid are clearly stated.  This work does not supersede the A/E’s review of the O&M manuals according to the A/E’s contract.

D.	The Contractor shall compile O&M manuals for every piece of equipment and building operating or electrical system being commissioned with the following format.

- Quantity: 6 (Unless more are required by the Technical Specifications)

- Format: 8 1/2 x 11 3 ring loose-leaf binders, 3inch maximum, and electronic format that is compatible with Owners system.  Each binder shall be clearly labeled on the spine.  Use as many binders as required.  Do not overload binders.  Dividers with permanently marked tabs of card stock shall separate each section and sub section.  Tab labels shall not be handwritten.  A separate manual or chapter shall be provided for each applicable system as follows:

- Chillers (by type).

- Pumps.

- Bridge-Tender System

- Air Handling Units (include Sequence of Operation, one line diagram and area served in a plastic pouch for mounting on equipment or in equipment room).

- Exhaust Fans.

- Supply Air Fans (excluding Air Handling Units).

- Vibration Monitoring System.

- Cooling Towers.

- Preconditioned Air System.

- 400-Hertz System.

- Plumbing and Drainage Systems/Equipment.

- Emergency Generator Systems.

- UPS

- Fire Protection Systems.

- Fire Alarm System.

- Valves and Pipe Specialties (include valve identification chart).

- Variable Frequency Drives (VFD).

- Ice Storage System.

- Smoke Control Systems.

- Water Treatment System.

- Kitchen/Cooking/Food Preparation Systems.

- Escalator/Elevator Systems.

- People Mover Systems.

- Baggage Conveyors, Make-up and Claim Systems.

- Lighting Systems and Controls (interior, exterior and airfield).

- Switchgear, Transformers, Panel boards, Motor Control Centers and Motor Starters.

- Lightning Protection and Surge Suppression Systems.

- Public Address, Closed Circuit TV, Flight Information Display and Telephone Systems.

- Security System.

- Loading Bridges.

- Building Management/Temperature Control System

- Fuel System

- Doors and Hardware.

- Irrigation

- Walk-in Coolers and Freezers

- Power monitoring systems

- HVAC, Testing Adjusting, and Balancing

- Other ___________.

3.	There shall be a title page and table of contents in the front of each binder for each binder’s contents.  In each binder, there shall be a main tab for each specification section.  Behind the section number tab there shall be the equipment ID tag sub-tab for each piece of major equipment (or group, if small or numerous).  These sub-tabs shall be similar to the specification number tabs but of a different color.  Behind each equipment name tab shall be the following sections, in the given order, divided by a double weight colored sheet labeled with the title of the section.

(a)	Contractor.  The first page behind the equipment tab shall contain the name, address and telephone number of the manufacturer and installing contractor and the 24-hour number for emergency service for all equipment in this section, identified by equipment.

(b)	Submittal and Product Data.  This section shall include all approved submittal data, cut sheets, data base sheets and appropriate shop drawings.  If submittal was not required for approval, descriptive product data shall be included.

(c)	Operation and Maintenance Instructions.  These shall be the written manufacturer’s data with the model and features of this installation clearly marked and edited to omit reference to products or data not applicable to this installation.  This section shall include data on the following:

(1)	Model number, serial number and nameplate data for each piece of equipment and any subcomponent.

(2)	Installation, startup and break-in instructions.

- All starting, normal shutdown, emergency shutdown, manual operation and normal and emergency operating procedures and data, including any special limitations.

i.	Step-by-step procedure for system start-up, including a pre-start checklist.  Refer to controls and indicators by nomenclature consistent with that used on panels and in control diagrams.

ii.	Sequence of Operation, with detailed instruction in proper sequence, for each mode of operation (i.e., day-night; staging of equipment).

iii.	Emergency Operation:  If some functions of the equipment can be operated while other functions are disabled, give instructions for operations under these conditions.  Include here only those alternate methods of operations (from normal) which the operator can follow when there is a partial failure or malfunctioning of components, or other unusual condition.

iv.	Shutdown Procedure:  Include instructions for stopping and securing the equipment after operation.  If a particular sequence is required, give step-by-step instructions in that order.

- O&M and installation instructions that were shipped with the unit.

- Preventative and corrective maintenance, with service procedures and schedules:

i.	Provide a schedule for preventive maintenance in a printed format and an electronic format compatible with owners system. State, preferably in tabular form, the recommended frequency of performance for each preventive maintenance task, cleaning, inspection and scheduled overhauls.

ii.	Cleaning:  Provide instructions and schedules for all routine cleaning and inspection with recommended lubricants.

iii.	Inspection:  If periodic inspection of equipment is required for operation, cleaning or other reasons, indicate the items to be inspected and give the inspection criteria for: motors; controls; filters and any other maintenance items.

iv.	Provide instructions for minor repairs or adjustments required for preventive maintenance routines.  Identify test points and give values for each.  Include sensor calibration requirements and methods by sensor type.

v.	Corrective maintenance instructions shall be predicated upon a logical effect-to-cause troubleshooting philosophy and a rapid replacement procedure to minimize equipment downtime.

- Troubleshooting:  Troubleshooting tables, charts, or diagrams shall be used to present specified procedures.  A guide to this type shall be a three-column chart.  The columns shall be titled:  Malfunction, Probable Cause and Recommended Action.

- Repair and Replacement:  Indicate repair and replacement procedures most likely to be required in the maintenance of the equipment.

(6)	Safety Precautions:  This subsection shall comprise a listing of safety precautions and instructions to be followed before, during and after making repairs, adjustments or routine maintenance.

(7)	Manufacturers' brochures (including controls):  Manufacturers' descriptive literature covering devices and equipment used in the system, together with illustrations, exploded views and renewal parts lists.  Manufacturers’ standard brochures and parts list shall be corrected so that information applying to the actual installed equipment is clearly defined.

(8)	Supply any special tools required to service or maintain the equipment.

(9)	Performance data, ratings and curves.

(10)	Warranty and Guarantee, which clearly lists conditions to be maintained to keep warranty in effect and conditions that would affect the validity of the warranty.

(11)	Any service contracts issued.

(d)	Supplemental Data.  Prepare written text and/or special drawings to provide necessary information, where manufacturer’s standard printed data is not available and information is necessary for a proper understanding and operation and maintenance of equipment or systems, or where it is necessary to provide additional information to supplement data included in the manual or project documents.

- Control Diagrams/Drawings.  Include the as-built control diagrams/drawings for the piece of equipment and its components, including full points list, full print out of all schedules and set points after testing and acceptance of the system, and copies of all checkout tests and calibrations performed by the Contractor (not commissioning tests).

(f)	Specifications.  This section is comprised of the component or system specification section copied and inserted complete with all addenda.

(g)	System Description.  This section shall include the individual equipment portion of the overall system Design Basis Narrative.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

Controls, and Test, Adjust, and Balance (TAB) O&M Manuals.  The controls contractor and TAB contractor have special O&M manual preparation requirements identified in Technical Specifications. The A/E shall coordinate those requirements with those of this section.

The A/E shall include in the beginning of the O&M manuals a separate section describing the systems including:

a.	The design intent narrative prepared by the A/E and provided as part of the bid documents, updated to as-built status by the A/E.

b.	Simplified professionally drawn single line system diagrams on  8 1/2 x 11 or 11 x 17 sheets.

* * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * * *

END OF SECTION