Specification Section 15_____

### Project: __________________________________	Project No: __________

Components included:

___supply fan(s), ___ return fan(s), ___cooling coil(s),  ___valves,  ___dampers

Associated Checklists:

___CHW Piping, ___ exhaust fans, ___VAV boxes, ___ VFD/VIV, ___Other_______________________

1.	Submittal / Approvals

Submittal.  The above equipment and systems integral to them are complete and ready for functional testing.  The checklist items are complete and have been checked off only by parties having direct knowledge of the event, as marked below, respective to each responsible contractor.  This prefunctional checklist is submitted for approval, subject to an attached list of outstanding items yet to be completed.  A Statement of Correction will be submitted upon completion of any outstanding areas.  None of the outstanding items preclude safe and reliable functional tests being performed.	___ List attached.

_____________________    __________     _____________________   __________

Mechanical Contractor		Date		Controls Contractor		Date

_____________________    __________     _____________________   __________

Electrical Contractor		Date		Sheet Metal Contractor	Date

_____________________    __________     _____________________   __________

TAB Contractor			Date		General Contractor		Date

Prefunctional checklist items are to be completed as part of startup & initial checkout, preparatory to functional testing.

- This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

- Contractors assigned responsibility for sections of the checklist shall be responsible to see that checklist items by their subcontractors are completed and checked off.

Approvals.  This filled-out checklist has been reviewed.  Its completion is approved.

_____________________   __________         ____________________   __________

Commissioning Authority/Agent	Date		Owner’s Representative		Date

2.	Requested documentation submitted

- Manufacturer’s cut sheets:

Yes  /  No - date to be submitted _______

- Performance data (fan curves, coil data, etc.):

Yes  /  No - date to be submitted _______

- Installation and startup manual and plan:

Yes  /  No - date to be submitted _______

- Sequences and control strategies:	Yes  /  No - date to be submitted _______

- O & M Manuals:	Yes  /  No - date to be submitted _______

- Data base sheets:	Yes  /  No - date to be submitted _______

3.	Model Verification

| Item | Specified | Submitted | Installed |
| --- | --- | --- | --- |
| Manufacturer |  |  |  |
| Model |  |  |  |
| Serial Number |  |  |  |
| Capacity (BTU/Hr) |  |  |  |
| CFM (Total) |  |  |  |
| Volts/Phase |  |  |  |

- Installation Checks

- Unit and General Installation

  - Permanent labels affixed:	Yes   /   No

  - Casing condition good – no dents, leaks, door gaskets installed:	Yes   /   No

  - Access doors close tightly – no apparent leaks:	Yes   /   No

  - Flexible duct between unit and rigid duct tight; in good condition: 	Yes   /   No

  - Vibration isolation equipment installed and active:	Yes   /   No

  - Maintenance access acceptable for unit and components:	Yes   /   No

  - Sound attenuation installed (internal lining):	Yes   /   No

  - Thermal insulation installed properly:	Yes   /   No

  - Instrumentation installed correctly per specifications (thermometers, pressure gages, flow meters, transmitters, sensors):	Yes   /   No

  - Equipment clean:	Yes   /   No

  - Filters installed:	Yes   /   No

  - Filter housing installation allows for easy filter replacement:	Yes   /   No

  - Filters clean and tight fitting:	Yes   /   No

  - Filter pressure differential measuring device installed and functional (magnahelic, etc.):	Yes   /   No

  - Cosatron/electronic filtration installed:	Yes   /   No

  - Cosatron/electronic filtration operational:	N/A   /  Yes   /   No

- Valves, Piping and Coils

  - Pipe fittings complete and pipes properly supported:	Yes   /   No

  - Pipes properly insulated:	Yes   /   No

  - Pipes properly labeled:	Yes   /   No

  - Piping system properly flushed:	Yes   /   No

  - Piping system charged:	Yes   /   No

  - No leaking evident around fittings:	Yes   /   No

  - Coils are clean, fins are in good condition:	Yes   /   No

  - Condensate drain pan(s) installed, clean, sloped properly:	Yes   /   No

  - Condensate drain line(s) installed and supported correctly:	Yes   /   No

  - Control valve and isolation valves installed:	Yes   /   No

  - Valves properly labeled:	Yes   /   No

  - Valves installed in proper direction:	Yes   /   No

  - Outside air temperature, mixed air temperature, supply air temperature, return air temperature, chilled water supply/return sensors properly located and secure (related OA temperature sensor shielded:	Yes   /   No

  - Sensors calibrated (see calibration section below):	Yes   /   No

  - Pressure / temperature plugs and isolation valves installed per drawings):

Yes   /   No

- Fans and Dampers

  - Supply fan and motor alignment correct::	Yes   /   No

  - Supply fan belt tension and condition good:	Yes   /   No

  - Supply fan protective shrouds for belts in place and secure:	Yes   /   No

  - Supply fan area clean:	Yes   /   No

  - Supply fan and motor lube lines installed and lubed:	Yes   /   No

  - Return fan and motor alignment correct:	N/A  /  Yes   /   No

  - Return fan belt tension and condition good:	N/A  /  Yes   /   No

  - Return fan protective shrouds for belts in place and secure:	N/A  /  Yes  /  No

  - Return fan area clean:	N/A  /  Yes   /   No

  - Return fan and motor lube lines installed and lubed:	N/A  /  Yes   /   No

  - Exhaust fan checklists for service area complete: 	N/A  /  Yes   /   No

  - Smoke and fire dampers installed properly per contract docs (proper location, access doors, appropriate ratings verified):	Yes   /   No

  - All dampers close properly:	Yes   /   No

  - All dampers (outside air, return air, supply air) stroke fully without binding:

Yes   /  No

  - All damper linkages have minimum play:	Yes   /   No

- Duct

  - Sound attenuators/lining installed:	Yes   /   No

  - Duct joint sealant properly installed:	Yes   /   No

  - No apparent severe duct restrictions:	Yes   /   No

  - Turning vanes in square elbows as per drawings:	N/A  /  Yes   /   No

  - Outside air intakes located away from pollutant sources & exhaust outlets:

Yes   /   No

  - Pressure leakage tests completed:	Yes   /   No

  - Branch duct control dampers operable:	Yes   /   No

  - Ducts cleaned as per specifications:	Yes   /   No

  - VAV boxes installed, checklist complete:	Yes   /   No

  - Balancing dampers installed per drawings and TAB Contractor’s site visit:

Yes   /   No

  - Supply and return grilles/registers installed:	Yes   /   No

- Electrical and Controls

  - HOA switch installed and functioning:	Yes   /   No

  - DCP power source identified:	Yes   /   No

  - Panel labeled with permanent label:	Yes   /   No

  - Power disconnect in place and labeled:	Yes   /   No

  - Low voltage wiring in separate conduit as 120 vac:	Yes   /   No

  - 120 vac lightning protection installed:	Yes   /   No

  - Low voltage lightning protection installed (underground only): 	N/A  /  Yes / No

  - Pneumatic devices separated from controller and electronics:	Yes   /   No

  - E-O-L devices labeled and wiring tagged per drawings:	Yes   /   No

  - Panel devices labeled and wiring tagged per drawings:	Yes   /   No

  - I/O devices labeled and wiring tagged per drawings:	Yes   /   No

  - Digital inputs and outputs operational:	Yes   /   No

  - E-PROM images on LAN for each controller:	Yes   /   No

  - Controller drawing and point summary log in panel: 	Yes   /   No

  - All electric connections tight:	Yes   /   No

  - Proper grounding installed for components and unit:	Yes   /   No

  - Safeties in place and operable:	Yes   /   No

  - Starter overload breakers installed and correct size:	Yes   /   No

  - Sensors calibrated (see below) :	Yes   /   No

  - Control system interlocks hooked up and functional:	Yes   /   No

  - Smoke detectors in place:	Yes   /   No

  - All control devices, pneumatic tubing and wiring complete:	Yes   /   No

- VFD/VIV

  - VFD/VIV Checklist complete and approved:	Yes   /   No

- TAB

  - Installation of required system balancing devices complete:	Yes   /   No

- Final

  - Smoke/fire dampers and VAV boxes are open:	Yes   /   No

  - Startup report completed with this checklist attached:	Yes   /   No

  - Safeties and safe operating ranges for this equipment have been reviewed and accepted:	Yes   /   No

  - Sequence of Operation adequately show all information: 	Yes   /   No

  - Construction filters installed on return air grilles, to minimize dirt in the ductwork and coils and in any finished areas:	Yes   /   No

  - Verification of potential moisture migration has been performed via inspection of wall/building construction and review of operating sequences for all makeup air, supply, return (if applicable) and exhaust fans:	Yes   /   No

- Operational Checks  (These augment manufacturer’s list.  This is not the functional performance testing.)

- Supply fan rotation correct:	Yes   /   No

- Return fan rotation correct:	N/A   /   Yes   /   No

- Fans > 5 Hp Phase Checks

(%Imbalance = 100 x (avg. – lowest) / avg.)

Imbalance less than 2%?	Yes   /   No

- Record full load running amps for each fan.

SF Fan No. ____  :  _____rated FL amps x ______srvc factor = _______ (Max amps)

SF Fan No. ____  :  _____rated FL amps x ______srvc factor = _______ (Max amps)

SF Fan No. ____  :  _____rated FL amps x ______srvc factor = _______ (Max amps)

SF Fan No. ____  :  _____rated FL amps x ______srvc factor = _______ (Max amps)

RF Fan No. ____  :  _____rated FL amps x ______srvc factor = _______ (Max amps)

RF Fan No. ____  :  _____rated FL amps x ______srvc factor = _______ (Max amps)

RF Fan No. ____  :  _____rated FL amps x ______srvc factor = _______ (Max amps)

RF Fan No. ____  :  _____rated FL amps x ______srvc factor = _______ (Max amps)

All running less than max:	Yes   /   No

- Return fan acceptable noise & vibration:	N/A   /  Yes   /   No

- Supply fan has no unusual noise or vibration:	Yes   /   No

- Valves stroke fully and easily:	Yes   /   No

- Valves verified to not be leaking through coils when closed at normal operating pressure:	Yes   /   No

- The HOA switch properly activates and deactivates the unit:	Yes   /   No

- Specified sequences of operation and operating schedules have been implemented with all variations documented:	Yes   /   No

- Specified point-to-point checks have been completed and documentation record submitted for this system:	Yes   /   No

6.	Sensor and Actuator Calibration

All field-installed temperature, [relative humidity], [CO], [CO2] and pressure sensors and gages, and all actuators (dampers and valves) on this piece of equipment shall be calibrated.  Sensors installed in the unit at the factory with calibration certification provided need not be field calibrated.

All test instruments have had a certified calibration within the last 12 months:  Y/N______.

#### Sensor/Actuator Verification Table

(AHU in Operation)

| Sensor or Actuator | Location OK (Y/N) | Thermometer or Gage Value | BMS Value | Instrument Measured Value | Pass (Y/N) |
| --- | --- | --- | --- | --- | --- |
| SA Discharge |  |  |  |  |  |
| RA |  |  |  |  |  |
| OA |  |  |  |  |  |
| CHWR (@AHU) |  |  |  |  |  |
| CHWS (@AHU) |  |  |  |  |  |
| Duct SP (@SA Discharge) |  |  |  |  |  |
| CHW Control Valve Position |  |  |  |  |  |

Thermometer/Gage reading = reading of the permanent instrument on the equipment.  BMS = building management system.  Instrument = testing instrument.

All sensors are calibrated within required tolerances	___ YES   ___ NO

-- END OF CHECKLIST--