Specification Section 15_____

### Project: __________________________________	Project No: __________

Components included:

___ fan(s) and motor(s), ___basin(s), sump(s), distribution piping, ___fill,

___ Other_____________________________________

Associated Checklists:

___Pipe

___Pumps

___Other_______________________

1.	Submittal / Approvals

Submittal.  The above equipment and systems integral to them are complete and ready for functional testing.  The checklist items are complete and have been checked off only by parties having direct knowledge of the event, as marked below, respective to each responsible contractor.  This prefunctional checklist is submitted for approval, subject to an attached list of outstanding items yet to be completed.  A Statement of Correction will be submitted upon completion of any outstanding areas.  None of the outstanding items preclude safe and reliable functional tests being performed.	___ List attached.

_____________________    __________     _____________________   __________

Mechanical Contractor		Date		Controls Contractor		Date

_____________________    __________     _____________________   __________

Electrical Contractor		Date		Plumbing Contractor	Date

_____________________    __________     _____________________   __________

Fire Protection Contractor		Date		Structural Contractor	Date

_____________________    __________

General Contractor			Date

Prefunctional checklist items are to be completed as part of startup & initial checkout, preparatory to functional testing.

- This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

- Contractors assigned responsibility for sections of the checklist shall be responsible to see that checklist items by their subcontractors are completed and checked off.

Approvals.  This filled-out checklist has been reviewed.  Its completion is approved.

_____________________   __________         ____________________   __________

Commissioning Authority/Agent	Date		Owner’s Representative		Date

2.	Requested documentation submitted

- Manufacturer’s cut sheets:	Yes	/	No - date to be submitted _______

- Performance data (fan curves, sound, etc.):

Yes  /  No - date to be submitted _______

- Installation and startup manual and plan:

Yes  /  No - date to be submitted _______

- Sequences and control strategies:

Yes  /  No - date to be submitted _______

- O & M Manuals:	Yes	/	No - date to be submitted _______

- Data base sheets:	Yes	/	No - date to be submitted _______

- Model Verification

| Item | Specified | Submitted | Installed |
| --- | --- | --- | --- |
| Manufacturer |  |  |  |
| Type |  |  |  |
| Model |  |  |  |
| Serial Number |  |  |  |
| Total Capacity (tons) |  |  |  |
| Number of Cells |  |  |  |
| Structure/shell Material |  |  |  |
| Fill Material |  |  |  |

- Installation Checks

- General Installation

  - Cooling tower installed capacity matches specified:	Yes   /   No

  - Location per construction drawings:	Yes   /   No

  - Orientation per construction drawings:	Yes   /   No

  - Screening per construction drawings:	N/A  /  Yes   /   No

  - Discharge stack installed per construction drawings:	Yes   /   No

  - Fill installed per shop drawings:	Yes   /   No

  - Handrails, ladders, safety cages, stairs, platforms, access hatches and cat walks installed per construction drawings:	Yes   /   No

  - Equipment clean:	Yes   /   No

- Water Distribution, Valves and Piping (immediately in and around cooling tower)

  - Pipe (distribution, supply, sump and/or return, equalizer, make-up water) installed per shop drawings:	Yes   /   No

  - Distribution nozzles installed per shop drawings, with all nozzles in place:

Yes   /   No

  - Pipes supported per shop drawings, all supports in place and active:

Yes   /   No

  - Isolation valves installed per shop drawings:	Yes   /   No

  - Control valves installed per contract and shop drawings:	Yes   /   No

  - Wells for monitoring/control sensors, transmitters, and/or gages are installed correctly:	N/A  /  Yes   /   No

  - Monitoring/control sensors, transmitters, and/or gages are installed correctly:	N/A  /  Yes   /   No

  - Test ports installed per shop drawings for monitoring/control sensors/ transmitters:	N/A  /  Yes   /   No

  - As-built drawings updated:	Yes   /   No

  - Protective coating installed on pipe and supports/hangers per specifications:

N/A  /  Yes   /   No

  - Permanent identification installed:	Yes   /   No

- Fan(s), Motor(s), Couplings and Drive Shaft(s)

  - Fan(s) installed per shop drawings (including type, blades and speed):

Yes   /   No

  - Fan tip clearance to cell wall is per shop drawings and recorded below:

Yes   /   No

  - Pitch angle recorded below:	Yes   /   No

  - Fan is lubricated and lubrication points are accessible:	Yes   /   No

  - Motor type, horsepower, and voltage/phase per shop drawings: 	Yes   /   No

  - Motor type, horsepower, and voltage/phase per construction drawings and specifications:	Yes   /   No

  - Motor installed per shop drawings:	Yes   /   No

  - Motor installed per construction drawings:	Yes   /   No

  - Drive shaft installed per shop drawings:	Yes   /   No

  - Drive shaft bearings are lubricated and lubrication points are accessible:

N/A  /  Yes   /   No

  - Gear box and/or speed reducers installed per shop drawings:	  N/A  /  Yes  /  No

  - Spacer sleeve properly installed on output shaft:	N/A  /  Yes   /   No

  - Drive shaft/coupling hubs aligned, readings recorded below:	Yes   /   No

  - Gear box and/or speed reducers lubricated and lubrication points are accessible:	N/A  /  Yes   /   No

  - Lubrication sight gages installed, with correct levels, isolation/ball valves open:	N/A  /  Yes   /   No

- Electrical and Controls

  - HOA switch installed and functioning:	Yes   /   No

  - Panel power source identified:	Yes   /   No

  - Panel labeled with permanent label:	Yes   /   No

  - Power disconnect in place and labeled:	Yes   /   No

  - Low voltage wiring in separate conduit as 120 vac:	N/A  /  Yes   /   No

  - 120 vac lightning protection installed:	N/A  /  Yes   /   No

  - Low voltage lightning protection installed (underground only): 	N/A  /  Yes / No

  - Pneumatic devices separated from controller and electronics:	Yes   /   No

  - E-O-L devices labeled and wiring tagged per drawings:	Yes   /   No

  - Panel devices labeled and wiring tagged per drawings:	Yes   /   No

  - I/O devices labeled and wiring tagged per drawings:	Yes   /   No

  - Digital inputs and outputs operational:	Yes   /   No

  - E-PROM images on LAN for each controller:	Yes   /   No

  - Controller drawing and point summary log in panel: 	Yes   /   No

  - All electric connections tight:	Yes   /   No

  - Proper grounding installed for components and unit:	Yes   /   No

  - Safeties in place and operable:	Yes   /   No

  - Starter overload breakers installed and correct size:	Yes   /   No

  - Sensors calibrated (see below) :	Yes   /   No

  - Control system interlocks hooked up and functional:	Yes   /   No

  - All control devices, pneumatic tubing and wiring complete:	Yes   /   No

- VFD

  - VFD Checklist complete and approved:	N/A  /  Yes   /   No

  - VFD minimum speed set to insure proper drive shaft/gear box/speed reducer internal lubrication:	Yes   /   No

- Basin(s) and Sump(s)

  - Basin installed per drawings and specifications:	Yes   /   No

  - Basin slopes toward sump:	Yes   /   No

  - Basin water proofing installed per drawings and specifications:	Yes   /   No

  - Basin and sump area free of trash and debris:	Yes   /   No

  - Sump installed per drawings and specifications:	Yes   /   No

  - Sump water proofing installed per drawings and specifications:	Yes   /   No

  - Sump drain installed per on drawings and specifications:	Yes   /   No

  - Sump overflow pipe installed per on drawings and specifications:	Yes  /  No

- Accessories

  - Drift eliminators installed per shop drawings:	N/A  /  Yes   /   No

  - Drift eliminators are free of broken or loose bundles, loose support rods, and trash/debris on surface:	N/A  /  Yes   /   No

  - Air intake louvers installed per shop drawings:	N/A  /  Yes   /   No

  - Basin and/or sump covers installed per shop drawings:	N/A  /  Yes   /   No

  - Water treatment system installed per shop drawings:	Yes   /   No

- Fire Protection

    - Fire protection system installed per construction drawings and specifications: 	N/A  /  Yes   /   No

- Final

  - Pressure test complete with acceptable results per specifications:  Yes  /  No

  - Prefunctional testing complete for all connected equipment:	Yes   /   No

  - Flushing complete:	Yes   /   No

  - Water quality test complete:	N/A  /  Yes   /   No

  - Water quality test results accepted by MDAD:	N/A  /  Yes   /   No

  - Piping system charged:	Yes   /   No

  - Water treatment test results accepted:	N/A  /  Yes   /   No

  - Startup report completed with this checklist attached:	Yes   /   No

  - Safeties and safe operating ranges for this equipment have been reviewed and accepted:	Yes   /   No

  - Sequence of Operation adequately show all information:	Yes   /   No

  - System is ready for thermal performance testing: 	Yes   /   No

- Operational Checks  (These augment manufacturer’s list.  This is not the functional performance testing.)

- With motor disconnect “locked” in “off” position:

  - Shaft rotated by hand, with no binding:	Yes   /   No

  - All mounting bolts/set screws in place and tightened to specified torque value(s):

Yes   /   No

  - Gear reducer shaft rotated by hand, with no binding:	Yes   /   No

  - Fan blades track within one (1) inch:	Yes   /   No

  - Vibration sensors/switches connected:	Yes   /   No

  - Disconnect returned to “on” position:	Yes   /   No

- Fan(s) rotation correct:	Yes   /   No

- Motor Phase Checks

(%Imbalance = 100 x (avg. – lowest) / avg.)

Imbalance less than 2%?	Yes   /   No

- Record full load running amps for each motor per Table.  All running less than max:

Yes   /   No

- With fan(s) operated on low speed (for variable speed fans), noise and vibration are acceptable:	Yes   /   No

- With fan(s) operated on high speed (for variable speed fans), noise and vibration are acceptable:	Yes   /   No

- Vibration sensors/switches are set to account for start-up and/or speed changes thus preventing nuisance alarms/trips:	Yes   /   No

- Valves stroke fully and easily:	Yes   /   No

- Specified sequences of operation and operating schedules have been implemented with all variations documented:	Yes   /   No

- Specified point-to-point checks have been completed and documentation record submitted for this system:	Yes   /   No

6.	Sensor and/or Actuator Calibration

All field-installed temperature, [relative humidity] and pressure sensors and gages, and all actuators on this piece of equipment shall be calibrated.  Sensors installed in the unit at the factory with calibration certification provided need not be field calibrated.

All test instruments have had a certified calibration within the last 12 months:  Y/N______.

#### Sensor/Actuator Verification Table

| Sensor or Actuator | Location OK (Y/N) | Thermometer or Gage Value | BMS Value | Instrument Measured Value | Pass (Y/N) |
| --- | --- | --- | --- | --- | --- |
| Pressure ____ |  |  |  |  |  |
| Pressure ____ |  |  |  |  |  |
| Pressure ____ |  |  |  |  |  |
| Pressure ____ |  |  |  |  |  |
| Pressure ____ |  |  |  |  |  |
| Pressure ____ |  |  |  |  |  |
| Pressure ____ |  |  |  |  |  |
| CWR ___ |  |  |  |  |  |
| CWR ___ |  |  |  |  |  |
| CWR ___ |  |  |  |  |  |
| CWR ___ |  |  |  |  |  |
| CWR ___ |  |  |  |  |  |
| CWR ___ |  |  |  |  |  |
| CWS ___ |  |  |  |  |  |
| CWS ___ |  |  |  |  |  |
| CWS ___ |  |  |  |  |  |
| CWS ___ |  |  |  |  |  |
| CWS ___ |  |  |  |  |  |
| CWS ___ |  |  |  |  |  |

Thermometer/Gage reading = reading of the permanent instrument on the equipment.  BMS = building management system.  Instrument = testing instrument.

All sensors are calibrated within required tolerances	___ YES   ___ NO

-- END OF CHECKLIST--