Chilled Water System Pre-Operational Flushing and Treatment Procedure

PIPE - _________

Specification Section   _______

Project: __________________________________	Project No: __________

- Preparation

  - Bypass line between the main chilled water (CHW) return & supply lines to recirculate the entire system using the CHW pumps is installed:	Yes   /   No

  - All special treatment equipment listed in the specifications, such as a bypass feeder across a delta P of 5 PSIG or greater on ¾” piping, is installed: 	N/A  /   Yes   /   No

  - Potable water source to fill, dump and  flush all piping/associated equipment is connected per drawings/specifications: 	Yes   /   No

  - System has been filled with potable water and air bled from system: 	Yes   /   No

  - System has been dumped and flushed, at the lowest point, until all loose matter has been removed and water is clear for a minimum of 24 hours:	Yes   /   No

  - Interior of pipe has been inspected and/or video taped: 	Yes   /   No

  - System has been re-filled with potable water and air bled from the highest point on the loop:	Yes   /   No

- Pre-operational Cleaner

  - Project Manager and MDAD water treatment company notified for testing of loop (minimum 7 day notice is required): 	Yes   /   No

  - Up to 3% by volume of Ferroquest FQ7103( (Betzdearborn) pre-operational cleaner (or as stated in the specifications) has been added into the system:		Yes   /   No

- Recirculation and Pre-operational Treatment

  - System has been tested for total iron and pH per Table 1, with results recorded:		Yes   /   No

  - System has been re-circulated for a minimum of 72 hours after re-application of pre-operational cleaner, per Table 1: 	Yes   /   No

##### Table 1

| CONTROL LIMITS FOR FQ7103 PRE-OPERATIONAL CLEANER |
| --- |
| LOWER LIMITS | UPPER LIMITS |
| FIELD TESTS | DATE | DATE | DATE | VALUE | ACTION | VALUE | ACTION |
| TOTAL IRON |  |  |  | 0.0 | -- | 10,000 PPM | Dump & re-apply FQ7103 |
| PH |  |  |  | 6.0 | Drain & refill until 6.0 | 7.0 | Add more FQ7103, until pH remains at 6.7 |

- Pre-operational Testing

  - After pre-operational treatment parameters have been met (Table 1), system has been dumped and flushed (at its lowest point) until the water is clear (minimum of 24 hours): 		Yes   /   No

  - Field test parameters have been met and recorded in Table 2: 	Yes   /   No

##### Table 2

| TARGET FIELD VALUES OF FINAL PREOPERATIONAL FLUSH |
| --- |
| CHW LOWER LIMITS | CHW UPPER LIMITS |
| FIELD TESTS | MAKEUP | CHW Effluent | CHW Pass (Y/N) | FORMULA | RESULT | FORMULA | RESULT |
| CONDUCTIVITY |  |  |  | Makeup x 90% | umhos | Makeup x 110% | Umhos |
| TOTAL IRON |  |  |  |  | 0 PPM | Makeup x 150% | PPM |
| PH |  |  |  | Makeup x 97.5% | units | Makeup x 102.5% | Units |
| TURBIDITY |  |  |  | Makeup x 90% | FTU | Makeup x 110% | FTU |
| COLOR |  |  |  |  | CLEAR |  | CLEAR |

  - Lab test parameters have been met and recorded in Table 3: 	Yes   /   No

##### Table 3

| TARGET LAB VALUES OF FINAL PREOPERATIONAL FLUSH |
| --- |
| CHW LOWER LIMITS | CHW UPPER LIMITS |
| LAB TESTS | MAKEUP | CHW Effluent | CHW Pass (Y/N) | TARGET | TOLERANCE LIMITS | TARGET | TOLERANCE LIMITS |
| Freon extractables (O&G) |  |  |  | <1.0 PPM | 0 PPM | 1.0 PPM | 2.0 PPM |
| Total Iron |  |  |  | <0.1 PPM | 0 PPM | Makeup x 150% | 5.0 PPM |
| Conductivity |  |  |  | Makeup x 95% | 100 umhos | Makeup x 105% | 330 umhos |
| PH |  |  |  | Makeup x 95% | 7.0 units | Makeup x 105% | 9.5 units |
| Total Alkalinity |  |  |  | Makeup x 90% | 30 PPM | Makeup x 110% | 100 PPM |
| Calcium Hardness |  |  |  | Makeup x 90% | 30 PPM | Makeup x 110% | 120 PPM |
| Magnesium Hardness |  |  |  | Makeup x 90% | 5 PPM | Makeup x 110% | 30 PPM |
| Silica |  |  |  | Makeup x 90% | 0 PPM | Makeup x 110% | 20 PPM |
| Ryznar Saturation Index |  |  |  |  |  |  | 6.0 RSI |
| Langelier Saturation Index |  |  |  |  |  |  | +1.5 LSI |

  - System is ready for application of initial long term water treatment chemicals:		Yes   /   No

Comments: